## WRAMS 10020 Monitoring Point 1
WRAMS DISCHARGE DATA
ENVIRONMENTAL PROTECTION LICENCE 10020.
WRAMS MONITORING POINT 1
Monitoring Frequency | Daily during any discharge.
Method | Method approved in writing by the Authority.
Volume Limit | 1000 (kL per day).
Parameter / Pollutant | Daily Volume | Number of measurements | Mean Salinity | Number of measurements | Licensee Name | Sydney Olympic Park Authority.
Unit of measurement | (kL per Day) | N/A | (mS per cm) | N/A | Licensee Address | Locked Bag 3, SYDNEY OLYMPIC PARK, NSW 2127
100 percentile concentration limit |  |  |  |  | Location of Monitoring Point 1 | End pipe from Brickpit near footbridge over tributary of Haslams Creek.
Date Sampled
No discharges have occurred to date.
2020-07-27 | 244.8 | 3 | 638 | 3
2020-07-28 | 691.2 | 3 | 661 | 3
2020-07-29 | 691.2 | 3 | 719 | 3
2020-08-10 | 345.6 | 3 | 839 | 3
2020-08-11 | 432 | 3 | 836 | 3
2020-08-12 | 518.4 | 3 | 841 | 3
2020-08-13 | 230.4 | 3 | 890 | 3
2021-03-20 | 244.8 | 3 | 674 | 3
2021-03-21 | 691.2 | 3 | 679 | 3
2021-03-22 | 691.2 | 3 | 657 | 3
2021-03-23 | 691.2 | 3 | 640 | 3
2021-03-24 | 345.6 | 3 | 676 | 3
2021-09-03 | 357 | continuous | 1010 | continuous
2021-09-04 | 691 | continuous | 1025 | continuous
2021-09-05 | 691 | continuous | 1002 | continuous
2021-09-06 | 186 | continuous | 1073 | continuous
2021-09-13 | 357 | continuous | 1025 | continuous
2021-09-14 | 691 | continuous | 1015 | continuous
2021-09-15 | 691 | continuous | 1006 | continuous
2021-09-16 | 691 | continuous | 1092 | continuous
2021-09-17 | 691 | continuous | 1056 | continuous
2021-09-18 | 691 | continuous | 1023 | continuous
2021-09-19 | 691 | continuous | 1111 | continuous
2021-09-20 | 691 | continuous | 1048 | continuous
2021-09-21 | 403 | continuous | 1076 | continuous
2021-10-14 | 454 | continuous | 1035 | continuous
2021-10-15 | 691 | continuous | 1027 | continuous
2021-10-16 | 691 | continuous | 1055 | continuous
2021-10-17 | 691 | continuous | 1025 | continuous
2021-10-18 | 231 | continuous | 1032 | continuous
2021-11-10 | 501 | continuous | 1007 | continuous
2021-11-11 | 691 | continuous | 1018 | continuous
2021-11-12 | 691 | continuous | 1032 | continuous
2021-11-13 | 202 | continuous | 1024 | continuous
2021-11-26 | 484 | continuous | 998 | continuous
2021-11-27 | 691 | continuous | 1002 | continuous
2021-11-28 | 691 | continuous | 1015 | continuous
2021-11-29 | 691 | continuous | 1008 | continuous
2021-11-30 | 190 | continuous | 1080 | continuous
2022-02-22 | 344 | continuous | 979 | continuous
2022-02-23 | 691 | continuous | 964 | continuous
2022-02-24 | 691 | continuous | 953 | continuous
2022-02-25 | 691 | continuous | 948 | continuous
2022-02-26 | 691 | continuous | 932 | continuous
2022-02-27 | 691 | continuous | 919 | continuous
2022-02-28 | 691 | continuous | 919 | continuous
2022-03-01 | 691 | continuous | 916 | continuous
2022-03-02 | 691 | continuous | 905 | continuous
2022-03-03 | 691 | continuous | 873 | continuous
2022-03-04 | 691 | continuous | 856 | continuous
2022-03-05 | 691 | continuous | 854 | continuous
2022-03-06 | 691 | continuous | 853 | continuous
2022-03-07 | 691 | continuous | 839 | continuous
2022-03-08 | 691 | continuous | 821 | continuous
2022-03-09 | 691 | continuous | 767 | continuous
2022-03-10 | 691 | continuous | 762 | continuous
2022-03-11 | 202 | continuous | 758 | continuous
2022-03-19 | 432 | continuous | 760 | continuous
2022-03-20 | 691 | continuous | 757 | continuous
2022-03-21 | 691 | continuous | 726 | continuous
2022-03-22 | 691 | continuous | 754 | continuous
2022-03-23 | 691 | continuous | 757 | continuous
2022-03-24 | 432 | continuous | 754 | continuous
2022-03-28 | 403 | continuous | 743 | continuous
2022-03-29 | 691 | continuous | 745 | continuous
2022-03-30 | 691 | continuous | 745 | continuous
2022-03-31 | 691 | continuous | 742 | continuous
2022-04-01 | 691 | continuous | 738 | continuous
2022-04-02 | 691 | continuous | 735 | continuous
2022-04-03 | 691 | continuous | 735 | continuous
2022-04-04 | 691 | continuous | 737 | continuous
2022-04-05 | 691 | continuous | 740 | continuous
2022-04-06 | 691 | continuous | 738 | continuous
2022-04-07 | 691 | continuous | 730 | continuous
2022-04-08 | 691 | continuous | 705 | continuous
2022-04-09 | 215 | continuous | 702 | continuous
2022-05-16 | 376 | continuous | 689 | continuous
2022-05-17 | 362 | continuous | 691 | continuous
2022-05-21 | 441 | continuous | 679 | continuous
2022-05-22 | 691 | continuous | 682 | continuous
2022-05-23 | 691 | continuous | 681 | continuous
2022-05-24 | 691 | continuous | 679 | continuous
2022-05-25 | 255 | continuous | 680 | continuous
2024-06-03 | 684 | continuous | 0.592 | continuous
2024-06-04 | 691 | continuous | 0.587 | continuous
2024-06-05 | 691 | continuous | 0.591 | continuous
2024-06-06 | 691 | continuous | 0.59 | continuous
2024-06-07 | 691 | continuous | 0.588 | continuous
2024-06-08 | 691 | continuous | 0.587 | continuous
2024-06-09 | 691 | continuous | 0.596 | continuous
2024-06-10 | 691 | continuous | 0.588 | continuous
2024-06-11 | 691 | continuous | 0.588 | continuous
2024-06-12 | 691 | continuous | 0.588 | continuous
2024-06-13 | 691 | continuous | 0.585 | continuous
2024-06-14 | 340 | continuous | 0.585 | continuous
2024-06-15 | 0 | continuous | 0.022 | continuous
2024-06-16 | 0 | continuous | 0.018 | continuous
2024-06-17 | 0 | continuous | 0.017 | continuous
2024-06-18 | 0 | continuous | 0.018 | continuous
2024-06-19 | 0 | continuous | 0.015 | continuous
2024-06-20 | 0 | continuous | 0.016 | continuous
2024-06-21 | 0 | continuous | 0.016 | continuous
2024-06-22 | 305 | continuous | 0.581 | continuous
2024-06-23 | 691 | continuous | 0.581 | continuous
2024-06-24 | 691 | continuous | 0.585 | continuous
2024-06-25 | 691 | continuous | 0.576 | continuous
2024-06-26 | 691 | continuous | 0.584 | continuous
2024-06-27 | 691 | continuous | 0.584 | continuous
2024-06-28 | 224 | continuous | 0.577 | continuous
Units | Description
mS per cm | Millisiemens per centimeter - measure of conductivity across substrate surface.
kL per day | Kilolitres discharge daily for every discharge.
The WRAMS Licence can be viewed in full on the NSW EPA website:
http://www.epa.nsw.gov.au/prpoeoapp/ViewPOEOLicence.aspx?DOCID=29838&SYSUID=1&LICID=10020
NOTE: This document is available at www.sopa.nsw.gov.au and is uncontrolled once downloaded and/or printed.

## WRAMS 10020 Monitoring Point 2
WRAMS DISCHARGE DATA
ENVIRONMENTAL PROTECTION LICENCE 10020.
WRAMS MONITORING POINT 2
Monitoring Frequency | Daily during any discharge.
Method | Grab sample, and, method approved in writing by the Authority.
Volume Limit | 7000 (kL per day).
Parameter / Pollutant | Daily Volume | TSS | BOD | Faecal Coliforms | Total Phosphorus | Total Nitrogen | pH | Oil and Grease | Chlorine
Unit of measurement | (kL per Day) | (mg per L) | (mg per L) | (CFU per 0.1L) | (mg per L) | (mg per L) | (pH units) | (mg per L) | (mg per L)
80 percentile concentration limit | N/A | Nil | Nil | 1000 | Nil | Nil | Nil | Nil | Nil
90 percentile concentration limit | N/A | Nil | 40 | Nil | Nil | 10 | Nil | Nil | Nil
100 percentile concentration limit | N/A | 50 | 20 | 4000 | 1 | 12 | 6.5 - 8 | 10 | 0.5
Date Sampled | [9 empty] | Date Received | Date Published
2012-06-12 | 6920 | 16 | 4 | 740 | 0.89 | 1.6 | 8.09 | <5 | 0.3 | 2012-06-20 | 2012-07-11
2015-04-22 | 6000 | 20 | 3 | 200 | 0.8 | 3.7 | 8.13 | 5 | <0.2 | 2015-04-30 | 2015-06-16
2015-04-23 | 6000 | 12 | <2 | 130 | 0.94 | 3.2 | 8.19 | <5 | <0.2 | 2015-05-01 | 2015-06-16
2015-04-24 | 6000 | 8 | <2 | 64 | 0.94 | 3.2 | 8.05 | <5 | <0.2 | 2015-05-01 | 2015-06-16
2015-04-25 | 6000 | 12 | 3 | 11 | 1 | 1.4 | 8.04 | <5 | <0.2 | 2015-05-05 | 2015-06-16
2015-04-27 | 6000 | 12 | 3 | 11 | 1 | 1.4 | 8.04 | <5 | <0.2 | 2015-05-05 | 2015-06-16
2015-04-30 | 6000 | 8 | <2 | 100 | 0.9 | 3 | 8.21 | <5 | <0.2 | 2015-05-07 | 2015-06-16
2020-02-09 | 4833 | 13 | 5 | 140 | 0.33 | 1.5 | 7.95 | <5 | <0.2 | 2020-05-21
2020-02-10 | 4833 | 24 | 6 | 70 | 0.3 | 1.4 | 7.97 | 5 | <1 | 2020-05-21
2020-02-11 | 4833 | 13 | 3 | 160 | 0.8 | 1.2 | 8.01 | <5 | <0.2 | 2020-05-24
2020-02-12 | 4833 | 12 | 6 | 66 | 0.26 | 1.2 | 7.99 | <5 | <0.2 | 2020-05-24
2020-02-13 | 4833 | 11 | 8 | 52 | 0.27 | 1.2 | 7.51 | <5 | 0.08 | 2020-05-24
2020-07-27 | 4185 | <5 | 2 | 51 | 0.32 | 1.9 | 7.55 | <5 | <0.2 | 2020-08-03
2020-07-28 | 6480 | <5 | <2 | 30 | 0.35 | 1.8 | 7.62 | 5 | 0.03 | 2020-08-04
2020-07-29 | 2160 | <5 | 3 | 30 | 0.36 | 1.8 | 6.9 | <5 | 0.05 | 2020-08-05
2020-08-10 | 4050 | <5 | 2 | 26 | 0.34 | 1.6 | 7.93 | <5 | 0.08 | 2020-08-17
2020-08-11 | 6480 | <5 | 2 | 8 | 0.36 | 1.5 | 7.76 | <5 | 0.02 | 2020-08-19
2020-08-12 | 6480 | <5 | 3 | 16 | 0.4 | 1.8 | 7.14 | 5 | <0.2 | 2020-08-19
2020-08-13 | 6480 | <5 | 2 | 11 | 0.32 | 2 | 7.22 | <5 | <0.2 | 2020-08-20
2021-03-20 | 2295 | 7 | <2 | 160 | 0.5 | 1.5 | 7.66 | <5 | 0.21 | 2021-03-29
2021-03-21 | 6480 | 11 | 2 | 160 | 0.43 | 1.4 | 7.77 | <5 | 0.24 | 2021-03-29
2021-03-22 | 6480 | 11 | <2 | 110 | 0.44 | 1.5 | 7.8 | <5 | 0.2 | 2021-03-29
2021-03-23 | 6480 | 10 | 29 | 40 | 0.41 | 1.5 | 7.89 | <5 | 0.13 | 2021-03-30
2021-03-24 | 6480 | 10 | 7 | 58 | 0.45 | 1.5 | 7.87 | <5 | 0.13 | 2021-03-30
2022-02-24 | 4050 | 11 | 5 | 520 | 0.35 | 1 | 7.34 | <5 | 0.41 | 2022-03-02
2022-06-24 | 2160 | 8 | 2 | 290 | 0.32 | 0.9 | 7.68 | <5 | 0.42 | 2022-03-07
2022-02-27 | 3645 | 10 | <2 | 88 | 0.29 | 0.8 | 7.82 | <5 | 0,4 | 2022-03-07
2022-02-28 | 6480 | 11 | <2 | 170 | 0.3 | 0.8 | 7.78 | <5 | 0.39 | 2022-03-07
2022-03-01 | 6480 | 9 | <2 | 70 | 0.35 | 1 | 7.6 | <5 | 0.37 | 2022-03-08
2022-03-03 | 6480 | 10 | 2 | 110 | 0.31 | 0.9 | 7.55 | <5 | 0.3 | 2022-03-10
2022-03-04 | 6480 | 10 | 2 | 74 | 0.24 | 0.7 | 7.81 | <5 | 0.3 | 2022-03-11
2022-03-05 | 6480 | 8 | <2 | 18 | 0.4 | 0.8 | 7.69 | <5 | 0.28 | 2022-03-14
2022-03-07 | 4590 | <5 | <2 | 44 | 0.31 | 0.8 | 7.63 | <5 | 0.26 | 2022-03-14
2022-03-08 | 6480 | 6 | 4 | 34 | 0.23 | 0.9 | 7.95 | <5 | 0.22 | 2022-03-16
2022-03-09 | 6480 | 11 | 3 | 39 | 0.17 | 0.7 | 8.02 | 5 | 0.17 | 2022-03-16
2022-03-10 | 6480 | 8 | <2 | 40 | 0.18 | 0.5 | 7.51 | <5 | <0.2 | 2022-03-17
2022-04-07 | 3105 | 7 | 3 | 45 | 0.22 | 0.5 | 7.95 | <5 | 0.09 | 2022-04-19
2022-04-08 | 6480 | 8 | 3 | 48 | 0.21 | 0.5 | 7.65 | <5 | 0.18 | 2022-04-19
2022-07-03 | 5762 | 6 | 3 | 68 | 0.21 | 1 | 7.6 | <5 | <0.2 | 2022-07-11
2022-07-04 | 6931 | 7 | 2 | 52 | 0.2 | 1 | 7.85 | <5 | <0.2 | 2022-07-11
2022-07-05 | 6931 | 5 | 2 | 63 | 0.18 | 1 | 7.99 | <5 | <0.2 | 2022-07-13
2022-07-06 | 6931 | 6 | 2 | 64 | 0.18 | 1 | 7.99 | <5 | <0.2 | 2022-07-13
2022-07-07 | 6931 | <5 | <2 | 46 | 0.2 | 1.1 | 7.97 | <5 | <0.2 | 2022-07-14
Units | Description | [6 empty] | Licensee Name | Sydney Olympic Park Authority.
mg per L | Milligrams per Litre - the amount, in milligrams, of a pollutant per litre of substrate measured. | [6 empty] | Licensee Address | Locked Bag 3, SYDNEY OLYMPIC PARK, NSW 2127
CFU per 0.1L | Colony Forming Units per one hundred millilitres of substrate. | [6 empty] | Location of Monitoring Point 2 | Wier in gabion wall at the discharge end of the Eastern Water Quality Control Pond.
kL per day | Kilolitres discharge daily for every discharge.
The WRAMS Licence can be viewed in full on the NSW EPA website:
http://www.epa.nsw.gov.au/prpoeoapp/ViewPOEOLicence.aspx?DOCID=29838&SYSUID=1&LICID=10020
NOTE: This document is available at www.sopa.nsw.gov.au and is uncontrolled once downloaded and/or printed.

## WRAMS 10020 Monitoring Point 3
WRAMS MONTHLY DATA
ENVIRONMENTAL PROTECTION LICENCE 10020.
WRAMS MONITORING POINT 3
Monitoring Frequency | Monthly.
Method | Grab sample.
Pollutant | Aluminium | Ammonia | Boron | Conductivity | Copper | Manganese | Oil and Grease | Reactive Phosphorus | Sulfate | TKN | Zinc | Oxidised Nitrogen | BOD | TSS | Total Phosphorus
Unit | (mg per L) | (mg per L) | (mg per L) | (µs/cm) | (mg per L) | (mg per L) | (mg per L) | (mg per L) | (mg per L) | (mg per L) | (mg per L) | (mg per L) | (mg per L) | (mg per L) | (mg per L)
100 percentile concentration limit
Date Sampled | [15 empty] | Date Received | Date Published
2012-04-24 | 0.1 | 0.11 | 0.14 | 2640 | 0.012 | 0.088 | <5 | 1.04 | 204 | 3.1 | 0.079 | 7.4 | <2 | <5 | 1.78 | 2012-04-24 | 2012-05-25
2012-05-29 | 0.1 | 0.25 | 0.17 | 2760 | 0.021 | 0.124 | <5 | 6.64 | 9 | 4.4 | 0.116 | 15.1 | 3 | 6 | 7.81 | 2012-06-05 | 2012-07-11
2012-06-26 | 0.08 | 0.21 | 0.15 | 2630 | 0.018 | 0.056 | <5 | 3.48 | 168 | 3.6 | 0.101 | 15.2 | <2 | <5 | 3.9 | 2012-07-04 | 2012-07-11
2012-07-30 | 0.13 | 0.84 | 0.16 | 2580 | 0.02 | 0.097 | <5 | 2.52 | 165 | 11.4 | 0.138 | 23.2 | <2 | <5 | 3.45 | 2012-08-06 | 2012-08-08
2012-08-28 | 0.08 | 3.73 | 0.13 | 3260 | 0.014 | 0.059 | <5 | 1.93 | 204 | 7.9 | 0.094 | 13.1 | <2 | <5 | 2.47 | 2012-09-04 | 2012-09-10
2012-09-17 | 0.1 | 2.12 | 0.18 | 3480 | 0.021 | 0.085 | <5 | 1.44 | 207 | 7.2 | 0.144 | 21.7 | <2 | <5 | 1.9 | 2012-09-24 | 2012-09-08
2012-10-30 | 0.09 | 0.53 | 0.16 | 5200 | 0.018 | 0.003 | <5 | 3.07 | 274 | 3.3 | 0.087 | 1.26 | 3 | <5 | 4.06 | 2012-11-05 | 2012-11-13
2012-11-26 | 0.14 | 1.6 | 2.71 | 5100 | 0.022 | 0.081 | <5 | 3.43 | 264 | 6.7 | 0.089 | 10.8 | <2 | <5 | 3.64 | 2012-12-03 | 2012-12-20
2012-12-18 | 0.12 | 0.12 | 0.14 | 4710 | 0.02 | 0.013 | <25 | 3.54 | 271 | 8 | 0.071 | 6.9 | <2 | 6 | 4.14 | 2012-12-28 | 2013-01-08
2013-01-30 | 0.11 | 0.21 | 0.16 | 3680 | 0.017 | 0.04 | <5 | 5.37 | 289 | 6.4 | 0.1 | 10.2 | 4 | <5 | 5.87 | 2013-02-05 | 2013-02-07
2013-02-26 | 0.08 | 0.33 | 0.14 | 4350 | 0.015 | 0.005 | <5 | 4.14 | 260 | 3.2 | 0.041 | 4.54 | 8 | <5 | 4.16 | 2013-03-05 | 2013-03-06
2013-03-26 | 0.1 | 0.07 | 0.14 | 3830 | 0.013 | 0.009 | <5 | 4.06 | 253 | 3.4 | 0.052 | 8.93 | 7 | <5 | 4.67 | 2013-04-04 | 2013-04-18
2013-04-30 | 0.14 | 0.33 | 0.24 | 4290 | 0.021 | 0.136 | <5 | 3.14 | 274 | 4 | 0.121 | 6.8 | <2 | 5 | 3.26 | 2013-05-06 | 2013-05-20
2013-05-04 | 0.02 | 0.08 | 0.13 | 3920 | 0.01 | 0.003 | <5 | 3.88 | 230 | 2.3 | 0.035 | 2.76 | <2 | <5 | 3.73 | 2013-06-11 | 2013-06-12
2013-06-25 | 0.04 | 5.22 | 0.14 | 4280 | 0.014 | 0.007 | <5 | 4 | 211 | 5.4 | 0.037 | 3.76 | <2 | <5 | 4.46 | 2013-07-02 | 2013-07-08
2013-07-30 | 0.03 | 13.8 | 0.12 | 4020 | 0.015 | 0.065 | <5 | 3.4 | 240 | 19.1 | 0.06 | 7.48 | <2 | <5 | 3.85 | 2013-08-06 | 2013-08-06
2013-08-30 | 0.12 | 0.09 | 0.15 | 3950 | 0.026 | 0.164 | <5 | 2.16 | 249 | 38.9 | 0.182 | 31.5 | 8 | 20 | 3.37 | 2013-09-05 | 2013-09-09
2013-09-27 | 0.1 | 0.56 | 0.18 | 4840 | 0.018 | 0.034 | <5 | 4.17 | 276 | 8 | 0.108 | 15.4 | 12 | <5 | 4.32 | 2013-10-03 | 2013-10-16
2013-10-25 | 0.16 | 0.06 | 0.16 | 4840 | 0.024 | 0.033 | <5 | 4.44 | 273 | 5 | 0.088 | 10.4 | 4 | <5 | 5.05 | 2013-10-31 | 2013-11-04
2013-11-29 | 9.77 | 1.29 | 0.06 | 18600 | 1.55 | 1.58 | <5 | 0.89 | 58 | 25.4 | 0.257 | 0.73 | 17 | 64 | 4.34 | 2013-12-09 | 2013-12-13
2013-12-16 | 0.14 | 0.62 | 0.23 | 3790 | 0.015 | 0.098 | <5 | 3.35 | 260 | 7.4 | 0.079 | 10.4 | 5 | <5 | 4.02 | 2013-12-24 | 2014-01-09
2013-12-27 | 0.16 | 0.08 | 0.14 | 3200 | 0.011 | 0.053 | <5 | 2.86 | 188 | 3.3 | 0.045 | 2.14 | 5 | 7 | 3.31 | 2014-01-08 | 2014-01-09
2014-01-31 | 0.1 | 0.46 | 0.14 | 4040 | 0.011 | 0.028 | <5 | 3.06 | 243 | 11.1 | 0.072 | 8.06 | <2 | 6 | 4 | 2014-02-07 | 2014-02-12
2014-02-07 | 0.06 | 0.59 | 0.12 | 4450 | 0.009 | 0.005 | <5 | 4.3 | 197 | 3.4 | 0.032 | 3.26 | <2 | <5 | 5.17 | 2014-02-17 | 2014-02-20
2014-03-07 | 0.06 | 0.11 | 0.14 | 3310 | 0.012 | 0.066 | <5 | 2.62 | 179 | 3.4 | 0.078 | 8.74 | <2 | <5 | 4.48 | 2014-03-17 | 2014-03-20
2014-04-04 | 0.12 | 0.46 | 0.13 | 2220 | 0.016 | 0.179 | 8 | 2.88 | 150 | 4.9 | 0.086 | 5.66 | 3 | <5 | 3.15 | 2014-04-14 | 2014-04-24
2014-05-09 | 0.04 | 5.88 | 0.13 | 4050 | 0.015 | 0.008 | <5 | 3.37 | 252 | 7.7 | 0.053 | 17.6 | <2 | 5 | 3.52 | 2014-05-16 | 2014-05-19
2014-06-06 | 0.04 | 0.28 | 0.17 | 3820 | 0.022 | 0.103 | <5 | 3.02 | 235 | 5.1 | 0.1 | 16.9 | <2 | 15 | 3.95 | 2014-06-13 | 2014-06-16
2014-07-04 | 0.04 | 7.15 | 0.13 | 3410 | 0.017 | 0.301 | <5 | 2.36 | 196 | 11.2 | 0.109 | 15.3 | 3 | <5 | 2.44 | 2014-07-11 | 2014-07-15
2014-08-08 | 0.12 | 0.85 | 0.1 | 2230 | 0.022 | 0.077 | <5 | 1.02 | 158 | 4.1 | 0.11 | 8.71 | <2 | <5 | 1.61 | 2014-08-15 | 2014-08-21
2014-09-05 | 0.1 | 0.62 | 0.1 | 1770 | 0.013 | 0.125 | <5 | 0.9 | 130 | 4.2 | 0.097 | 8.55 | 3 | 6 | 1.4 | 2014-09-12 | 2014-09-15
2014-10-03 | 0.08 | 0.4 | 0.08 | 2580 | 0.018 | 0.138 | <5 | 2.26 | 202 | 4.2 | 0.134 | 17 | <2 | <5 | 0.21 | 2014-10-10 | 2014-10-14
2014-11-07 | 0.07 | 0.09 | 0.13 | 3770 | 0.025 | 0.047 | <5 | 4.74 | 267 | 4.7 | 0.12 | 21.6 | <2 | <5 | 5.59 | 2014-11-17 | 2014-11-25
2014-12-05 | 0.1 | 0.25 | 0.14 | 3820 | 0.025 | 0.044 | <5 | 4.91 | 252 | 4.6 | 0.096 | 17.9 | 8 | <5 | 5.75 | 2014-12-15 | 2014-12-17
2015-01-09 | 0.09 | 0.06 | 0.11 | 4220 | 0.02 | 0.004 | <5 | 4.97 | 274 | 2.8 | 0.057 | 6.4 | <2 | 5 | 5.75 | 2015-01-19 | 2015-01-20
2015-02-06 | 0.68 | 0.08 | 0.06 | 16300 | 0.584 | 0.304 | <5 | 0.2 | 65 | 9.6 | 0.112 | 1.88 | <2 | 48 | 2.06 | 2015-02-17 | 2015-02-18
2015-03-06 | 0.1 | 0.08 | 0.1 | 3530 | 0.014 | 0.002 | <5 | 4.72 | 216 | 2.3 | 0.054 | 7.08 | <2 | 7 | 4.84 | 2015-03-16 | 2015-03-23
2015-04-10 | 0.06 | 0.07 | 0.12 | 3600 | 0.019 | 0.001 | <5 | 4.78 | 205 | 13 | 0.079 | 9.72 | <2 | <5 | 5.04 | 2015-04-17 | 2015-04-17
2015-05-08 | 0.09 | 0.09 | 0.25 | 2770 | 0.021 | 0.058 | <5 | 3.34 | 226 | 4 | 0.136 | 13.9 | <2 | <5 | 4.34 | 2015-05-18 | 2015-05-20
2015-06-05 | 0.04 | 0.58 | 0.1 | 2800 | 0.017 | 0.001 | <5 | 3.54 | 169 | 2.8 | 0.052 | 5.75 | <2 | <5 | 3.78 | 2015-06-15 | 2015-06-16
2015-07-10 | 0.11 | 0.12 | 0.16 | 2370 | 0.019 | 0.113 | <5 | 3.2 | 181 | 2.6 | 0.12 | 21.7 | <2 | <5 | 3.32 | 2015-07-16 | 2015-07-17
2015-08-07 | 0.03 | <0.01 | 0.1 | 2760 | 0.012 | 0.002 | <5 | 3.57 | 185 | 3.5 | 0.052 | 10.7 | <2 | <1 | 3.75 | 2015-08-14 | 2015-08-25
2015-09-11 | 0.07 | 0.08 | 0.09 | 2650 | 0.013 | 0.001 | <5 | 2.41 | 175 | 2.5 | 0.068 | 12.1 | <2 | <5 | 2.62 | 2015-09-11 | 2015-09-16
2015-10-02 | 0.14 | 0.1 | 0.09 | 3100 | 0.037 | 0.004 | <5 | 2.37 | 204 | 7.5 | 0.067 | 13.2 | <2 | 6 | 3.21 | 2015-10-12 | 2015-10-14
2015-11-06 | 0.05 | 0.32 | 0.11 | 3990 | 0.018 | 0.002 | <5 | 2.85 | 294 | 3 | 0.074 | 17 | <2 | <1 | 3.12 | 2015-11-16 | 2015-11-18
2015-12-11 | 0.13 | 0.29 | 0.1 | 2700 | 0.014 | 0.048 | <5 | 1.1 | 277 | 8.2 | 0.118 | 22.8 | <2 | <1 | 1.68 | 2015-12-21 | 2015-01-07
2016-01-09 | 0.04 | 0.19 | 0.07 | 2930 | 0.01 | 0.007 | <5 | 1.81 | 231 | 4.3 | 0.058 | 10.3 | <2 | 1 | 2.45 | 2016-01-18 | 2016-01-18
2016-02-05 | 0.07 | 0.1 | 0.12 | 3570 | 0.012 | 0.002 | <5 | 2.53 | 279 | 3.4 | 0.065 | 9.86 | <2 | <5 | 3.16 | 2016-02-12 | 2016-02-24
2016-03-11 | 0.15 | 0.04 | 0.12 | 3460 | 0.013 | 0.02 | <5 | 1.98 | 307 | 4.8 | 0.106 | 14.9 | <2 | 6 | 2.78 | 2016-03-17 | 2016-03-23
2016-04-08 | 0.12 | 0.02 | 0.23 | 3390 | 0.012 | <0.001 | <5 | 2.37 | 233 | 2.3 | 0.051 | 8.02 | <2 | 6 | 2.91 | 2016-04-14 | 2016-04-15
2016-05-13 | 0.04 | 0.02 | 0.1 | 3490 | 0.014 | 0.002 | <5 | 2.1 | 221 | 2.5 | 0.072 | 11.2 | <2 | <5 | 2.46 | 2016-05-20 | 2016-06-01
2016-06-10 | 0.02 | 0.73 | 0.08 | 2690 | 0.011 | 0.002 | <5 | 1.36 | 167 | 2.6 | 0.053 | 9.88 | <2 | 6 | 1.91 | 2016-06-20 | 2016-06-22
2016-07-01 | 0.1 | 0.14 | 0.1 | 2180 | 0.016 | 0.065 | <5 | 2.76 | 218 | 13.4 | 0.082 | 21.8 | <2 | <5 | 2.68 | 2016-07-07 | 2016-07-08
2016-08-05 | 0.04 | 0.27 | 0.08 | 2460 | 0.011 | 0.001 | <5 | 1.32 | 161 | 2.4 | 0.054 | 10.5 | <2 | <5 | 1.8 | 2016-08-11 | 2016-08-12
2016-09-02 | 0.09 | 0.05 | 0.07 | 2570 | 0.01 | <0.001 | <5 | 1.48 | 190 | 2.3 | 0.053 | 11.8 | <2 | <5 | 2.25 | 2016-09-08 | 2016-09-13
2016-10-07 | 0.07 | 0.08 | 0.11 | 3120 | 0.011 | <0.001 | <5 | 1.72 | 245 | 3.8 | 0.058 | 12.2 | <2 | 6 | 1.68 | 2016-10-13 | 2016-10-21
2016-11-04 | 0.08 | 0.2 | 0.1 | 3250 | 0.011 | <0.001 | <5 | 1.79 | 178 | 2.4 | 0.067 | 12.1 | <2 | <5 | 2.11 | 2016-11-10 | 2016-11-11
2016-12-02 | 0.12 | 0.34 | 0.1 | 2880 | 0.015 | 0.072 | <5 | 1.32 | 244 | 5.3 | 0.096 | 15 | <2 | 6 | 1.99 | 2016-12-09 | 2016-12-13
2017-01-13 | 0.34 | 0.14 | 0.13 | 3490 | 0.012 | 0.098 | <5 | 1.71 | 303 | 3.7 | 0.068 | 13.9 | <2 | 2 | 3.06 | 2017-01-20 | 2017-01-24
2017-02-03 | 0.3 | 0.05 | 0.12 | 3140 | 0.01 | 0.016 | <5 | 1.16 | 242 | 2.6 | 0.06 | 7.92 | <2 | 8 | 1.46 | 2017-02-09 | 2017-02-14
2017-03-03 | 0.14 | 0.03 | 0.07 | 1530 | 0.008 | 0.008 | <5 | 0.34 | 68 | 2.1 | 0.045 | 6.11 | <2 | <5 | 0.68 | 2017-03-08 | 2017-03-30
2017-04-13 | 0.08 | 0.12 | 0.12 | 2970 | 0.019 | 0.032 | <5 | 1.5 | 232 | 2.8 | 0.096 | 16.9 | <2 | 10 | 1.46 | 2017-04-21 | 2017-05-11
2017-05-05 | 0.16 | 0.24 | 0.11 | 2810 | 0.015 | 0.032 | <5 | 0.63 | 249 | 4.9 | 0.137 | 15.3 | <2 | <5 | 0.8 | 2017-05-12 | 2017-05-22
2017-06-09 | 0.1 | 0.18 | 0.09 | 2110 | 0.013 | 0.064 | <5 | 0.35 | 212 | 2.4 | 0.106 | 12.3 | <2 | <5 | 1 | 2017-06-19 | 2017-06-20
2017-07-07 | 0.04 | 0.14 | 0.06 | 1770 | 0.012 | 0.038 | <5 | 1.05 | 120 | 2.6 | 0.069 | 11.3 | 2 | <5 | 1.8 | 2017-07-14 | 2017-07-20
2017-08-04 | 0.16 | 0.49 | 0.1 | 2420 | 0.013 | 0.069 | <5 | 0.42 | 160 | 5 | 0.125 | 26.6 | <2 | <5 | 1.34 | 2017-08-11 | 2017-08-17
2017-09-29 | 0.12 | 0.51 | 0.12 | 3080 | 0.01 | 0.093 | <5 | 0.74 | 200 | 3.9 | 0.076 | 10.4 | 4 | <5 | 2.32 | 2017-10-13 | 2017-10-25
2017-10-20 | 0.12 | 0.75 | 0.12 | 3030 | 0.01 | 0.071 | <5 | 0.87 | 217 | 3.8 | 0.096 | 12 | <2 | <5 | 1.43 | 2017-10-26 | 2017-11-02
2017-11-10 | 0.1 | 0.18 | 0.12 | 2040 | 0.012 | 0.085 | <5 | 1.66 | 230 | 5.7 | 0.136 | 20.4 | <2 | <5 | 2.51 | 2018-11-17
2017-12-08 | 0.14 | 14.9 | 0.14 | 3170 | 0.013 | 0.186 | 7 | 1.14 | 230 | 15.7 | 0.08 | 16.5 | <2 | 5 | 1.96 | 2017-12-15 | 2017-12-15
2018-01-05 | 0.15 | 0.13 | 0.15 | 3140 | 0.008 | 0.127 | <5 | 0.6 | 224 | 3.1 | 0.085 | 9.35 | <2 | <5 | 0.98 | 2018-01-13 | 2018-02-06
2018-02-16 | 0.34 | 0.09 | 0.15 | 3930 | 0.015 | 0.024 | <5 | 1 | 234 | 3 | 0.069 | 6.68 | <2 | <5 | 1.84 | 2018-02-23 | 2018-02-27
2018-03-02 | 0.22 | 0.24 | 0.18 | 3260 | 0.014 | 1.71 | 68 | 1.15 | 236 | 2.6 | 0.134 | 15.1 | 4 | <5 | 2 | 2018-03-09 | 16/03/201
2018-03-14 | - | - | - | - | - | - | <5 | - | - | - | - | - | - | - | - | 2018-03-16 | 2018-03-28
2018-04-06 | 0.16 | 0.08 | 0.13 | 4660 | 0.014 | 0.002 | <5 | 1.37 | 291 | 3 | 0.041 | 6.8 | <2 | <5 | 1.49 | 2018-04-13 | 2018-05-17
2018-05-04 | 0.05 | 0.26 | 0.11 | 4090 | 0.01 | 0.014 | <5 | 1.62 | 272 | 2.3 | 0.052 | 9.2 | >2 | <5 | 2.32 | 2018-05-11 | 2018-05-17
2018-06-01 | 0.03 | 0.41 | 0.12 | 3840 | 0.014 | 0.232 | <5 | 2.44 | 243 | 2.3 | 0.062 | 12.9 | 2 | <5 | 2.81 | 2018-06-01 | 2018-06-18
2018-07-13 | 0.02 | 1.31 | 0.13 | 3250 | 0.017 | 0.234 | <5 | 2.22 | 238 | 2.6 | 0.09 | 12.4 | <2 | <5 | 2.36 | 2018-07-19 | 2018-08-07
August 2018 | No sampling and anaytical testing undertaken. Reverse osmosis facility was not operating in August due to maintenance works.
2018-09-14 | 0.04 | 2.41 | 0.1 | 3500 | 0.015 | 0.237 | <5 | 2.63 | 229 | 3.6 | 0.089 | 13.8 | <2 | 5 | 2.82 | 2018-09-20
2018-10-05 | 0.06 | 0.37 | 0.14 | 4260 | 0.019 | 0.04 | <5 | 2.87 | 376 | 3.4 | 0.096 | 16.4 | <2 | <5 | 3.32 | 2018-10-11 | 2018-11-01
2018-11-23 | 0.09 | 0.97 | 0.13 | 3440 | 0.017 | 0.055 | <5 | 1.17 | 292 | 3 | 0.084 | 6.92 | 2 | <5 | 1.35 | 2018-11-30 | 2018-12-06
2018-12-07 | 0.13 | 0.48 | 0.14 | 2910 | 0.01 | 0.151 | <5 | 0.79 | 285 | 3.6 | 0.0888 | 8.63 | 4 | <5 | 1.25 | 2018-12-14 | 2018-12-21
2019-01-04 | 0.18 | 0.61 | 0.14 | 3300 | 0.004 | 0.704 | <5 | 1.02 | 253 | 2.9 | 0.034 | 2.48 | 2 | <5 | 1.5 | 2019-01-11 | 2019-01-16
2019-02-01 | 0.38 | 0.06 | 0.14 | 3610 | 0.004 | 0.945 | <5 | 1.61 | 271 | 2.4 | 0.015 | 0.12 | 3 | <5 | 1.8 | 2019-02-11 | 2019-02-15
2019-03-01 | 0.56 | 0.09 | 0.15 | 3580 | 0.007 | 0.012 | <5 | 1.53 | 225 | 2.7 | 0.028 | 1 | <2 | 13 | 2.28 | 2019-03-08 | 2019-03-12
2019-04-05 | 0.26 | 0.03 | 0.15 | 4260 | 0.006 | 0.008 | <5 | 1.91 | 278 | 2.1 | 0.02 | 0.84 | <2 | <5 | 2.42 | 2019-04-11 | 2019-04-15
2019-05-03 | 0.14 | 0.84 | 0.13 | 4160 | 0.006 | 0.034 | 9 | 1.93 | 277 | 3 | 0.019 | 4.32 | <2 | 8 | 2.08 | 2019-05-09 | 2019-05-10
2019-06-07 | 0.02 | 0.08 | 0.12 | 3350 | 0.006 | 0.003 | <5 | 1.31 | 218 | 2.1 | 0.033 | 4.96 | <2 | 11 | 1.36 | 2019-06-14 | 2019-06-27
2019-07-05 | 0.02 | 0.28 | 0.13 | 3260 | 0.004 | 0.001 | <5 | 1.26 | 199 | 2.8 | 0.037 | 6.49 | <2 | <5 | 1.46 | 2019-07-11 | 2019-07-12
2019-08-02 | 0.02 | 0.8 | 0.12 | 3160 | 0.009 | <0.001 | <5 | 1.42 | 197 | 2.6 | 0.046 | 6.67 | <2 | <5 | 1.58 | 2019-08-07 | 2019-08-08
2019-09-06 | 0.04 | 2.73 | 0.12 | 3580 | 0.01 | 0.004 | <5 | 1.99 | 263 | 6.3 | 0.052 | 8.41 | 3 | 8 | 2.54 | 2019-09-13 | 2019-09-25
2019-10-04 | 0.03 | 0.55 | 0.16 | 3660 | 0.01 | 0.019 | <5 | 1.68 | 300 | 2.9 | 0.063 | 8.51 | <2 | <5 | 1.86 | 2019-10-14 | 2019-11-04
2019-11-08 | 0.09 | 0.07 | 0.11 | 3590 | 0.012 | 0.002 | <5 | 1.42 | 244 | 3 | 0.041 | 4.81 | <2 | 9 | 2.08 | 2019-11-15 | 2019-11-22
2019-12-13 | 0.32 | 0.18 | 0.15 | 3570 | 0.017 | 0.054 | <5 | 0.77 | 363 | 5.5 | 0.125 | 4.8 | 8 | <5 | 2.33 | 2019-12-20 | 2020-01-07
2020-01-03 | 0.42 | 0.35 | 0.15 | 4360 | 0.004 | 0.004 | <5 | 1.54 | 299 | 2.7 | 0.025 | 0.75 | <2 | <5 | 2.3 | 2020-01-09 | 2020-01-10
2020-02-07 | 0.16 | 0.26 | 0.17 | 3430 | 0.01 | 0.119 | <5 | 0.45 | 358 | 4.1 | 0.118 | 7 | <2 | <5 | 0.77 | 2020-02-14 | 2020-03-24
2020-03-06 | 0.12 | 0.14 | 0.16 | 3310 | 0.001 | 0.033 | <5 | 1.45 | 342 | 10 | 0.112 | 25.6 | 3 | 6 | 3.81 | 2020-03-13 | 2020-03-24
2020-04-03 | <0.01 | 0.01 | <0.05 | 19 | <0.001 | <0.001 | <5 | <0.01 | <1 | <0.1 | <0.005 | 0.22 | <2 | <5 | <0.01 | 2020-04-14 | 2020-04-16
2020-05-08 | 0.06 | 0.19 | 0.13 | 2420 | 0.016 | 0.099 | <5 | 3.42 | 245 | 2.9 | 0.088 | 20.6 | <2 | <5 | 2.95 | 2020-05-15 | 2020-05-20
2020-06-19 | 0.12 | 0.2 | 0.14 | 2420 | 0.017 | 0.071 | <5 | 2.17 | 227 | 3.2 | 0.126 | 16.3 | <2 | <5 | 2.38 | 2020-06-26 | 2020-06-26
2020-07-03 | 0.09 | 0.24 | 0.11 | 2380 | 0.012 | 0.056 | <5 | 1.46 | 232 | 3.1 | 0.112 | 13.7 | 2 | <5 | 2.1 | 2020-07-10 | 2020-07-16
2020-08-07 | 0.11 | 0.28 | 0.13 | 2710 | 0.008 | 0.083 | <5 | 0.8 | 287 | 5 | 0.109 | 13.8 | <2 | <5 | 1.13 | 2020-08-14 | 2020-08-28
2020-09-04 | 0.09 | 0.15 | 0.16 | 2920 | 0.014 | 0.067 | <5 | 0.96 | 264 | 3.2 | 0.108 | 13.7 | <2 | <5 | 1.43 | 2020-09-11 | 2020-09-17
2020-10-02 | 0.06 | 0.22 | 0.06 | 1980 | 0.008 | 0.021 | <5 | 0.91 | 151 | 1.9 | 0.062 | 6.26 | <2 | <5 | 1.29 | 2020-10-12 | 2020-10-16
2020-11-06 | 0.17 | 0.27 | 0.13 | 2230 | 0.015 | 0.081 | <5 | 0.78 | 274 | 2.5 | 0.168 | 19.3 | 3 | <5 | 1.63 | 2020-11-13 | 2020-11-19
2020-12-04 | 0.11 | 0.3 | 0.09 | 2960 | 0.009 | 0.212 | <5 | 0.94 | 250 | 2.8 | 0.101 | 14.8 | <2 | <5 | 1.38 | 2020-12-11 | 2020-12-16
2021-01-08 | 0.12 | 0.58 | 0.12 | 3580 | 0.013 | 0.315 | <5 | 1.51 | 282 | 8.4 | 0.097 | 25.2 | <2 | <5 | 2.22 | 2021-01-14 | 2021-01-20
2021-02-12 | 0.13 | 0.34 | 0.1 | 2620 | 0.013 | 0.077 | <5 | 0.56 | 265 | 5.7 | 0.141 | 24.7 | <2 | <5 | 1.19 | 2021-02-18
2021-03-05 | 0.17 | 0.4 | 0.12 | 3690 | 0.012 | 0.048 | <5 | 1.75 | 287 | 6 | 0.112 | 25.7 | <2 | <5 | 2.2 | 2021-03-12 | 2021-03-12
2021-04-01 | 0.09 | 7.42 | 0.1 | 2860 | 0.008 | 0.136 | <5 | 0.69 | 296 | 7.3 | 0.106 | 18.1 | <2 | <5 | 1.2 | 2021-04-12 | 2021-04-14
2021-05-14 | 0.08 | 0.48 | 0.09 | 2930 | 0.005 | 0.142 | <5 | 2.25 | 270 | 2.6 | 0.082 | 12.3 | <2 | <5 | 2.25 | 2021-05-24 | 2021-06-02
2021-06-04 | 0.11 | 0.08 | 0.1 | 2130 | 0.008 | 0.484 | <5 | 0.83 | 230 | 5.2 | 0.1 | 14.2 | <2 | <5 | 1.75 | 2021-06-15 | 2021-06-16
2021-07-02 | 0.06 | 0.13 | 0.07 | 1490 | 0.004 | 0.044 | <5 | 0.63 | 138 | 3.8 | 0.068 | 8.64 | <2 | <5 | 1.02 | 2021-07-09 | 2021-07-10
2021-08-06 | 0.07 | 0.13 | 0.07 | 1540 | 0.002 | 0.036 | <5 | 0.39 | 141 | 2 | 0.062 | 6.79 | <2 | <5 | 0.85 | 2021-08-13 | 2021-08-20
2021-09-10 | 0.14 | 0.23 | 0.1 | 2280 | 0.007 | 0.048 | <5 | 0.52 | 224 | 5.6 | 0.08 | 14.7 | <2 | <5 | 1.16 | 2021-09-17 | 2021-09-18
2021-10-01 | 0.1 | 0.33 | 0.1 | 2910 | 0.006 | 0.52 | <2 | 0.76 | 220 | 3.1 | 0.062 | 7.91 | 2 | 14 | 1.72 | 2021-10-11 | 2021-10-14
2021-11-12 | 0.11 | 0.1 | 0.42 | 2690 | 0.006 | 0.025 | <5 | 0.44 | 269 | 3.4 | 0.078 | 5.52 | <2 | <5 | 0.84 | 2021-11-19 | 2021-11-19
2021-12-03 | 0.08 | 0.14 | 0.12 | 2720 | 0.007 | 0.166 | <5 | 0.32 | 301 | 4.9 | 0.103 | 12.4 | <2 | <5 | 0.72 | 2021-12-14 | 2021-12-17
2022-01-14 | 0.06 | 0.14 | 0.06 | 2570 | 0.006 | 0.052 | <5 | 0.26 | 315 | 3.9 | 0.082 | 8.2 | <2 | 9 | 0.53 | 2022-01-22 | 2022-01-23
2022-02-03 | 0.07 | 0.11 | 0.09 | 2260 | 0.019 | 0.073 | <5 | 0.31 | 227 | 2.6 | 0.092 | 8.45 | <2 | <5 | 0.45 | 2022-02-10 | 2022-02-24
2022-03-17 | 0.08 | 0.15 | 0.14 | 2380 | 0.009 | 0.028 | <5 | 0.65 | 252 | 4.5 | 0.111 | 17.1 | <2 | <5 | 0.98 | 2022-03-24 | 2022-04-22
2022-04-07 | 0.07 | 0.27 | 0.08 | 3060 | 0.012 | 0.012 | <5 | 1.05 | 266 | 3.9 | 0.063 | 8.96 | <2 | <5 | 1.48 | 2022-04-14 | 2022-05-10
2022-05-05 | 0.09 | 0.25 | 0.23 | 2930 | 0.009 | 0.044 | <5 | 0.49 | 272 | 6.7 | 0.099 | 22.5 | <2 | <5 | 1.31 | 2022-05-12 | 2022-05-24
2022-06-02 | 0.1 | 0.16 | 0.12 | 3320 | 0.03 | 0.028 | <5 | 0.52 | 261 | 3.4 | 0.076 | 15 | <2 | <5 | 1.03 | 2022-06-09 | 2022-06-14
2022-07-14 | 0.14 | 0.24 | 0.17 | 3410 | 0.013 | 0.072 | 6 | 0.45 | 355 | 5.8 | 0.113 | 22.6 | 2 | <5 | 0.83 | 2022-07-21 | 2022-07-23
2022-08-04 | 0.17 | 0.34 | 0.16 | 3290 | 0.014 | 0.044 | <5 | 0.7 | 283 | 8.1 | 0.123 | 31.5 | <2 | <5 | 1.37 | 2022-08-12 | 2022-08-26
2022-09-01 | 0.14 | 0.19 | 0.13 | - | 0.009 | 0.075 | <5 | 0.53 | 259 | 4.3 | 0.096 | 16.6 | 2 | <5 | 0.98 | 2022-09-08 | 2022-09-10
2022-10-06 | 0.01 | 0.81 | 0.22 | 4610 | 0.004 | 0.01 | <5 | 1.15 | 281 | 3.4 | 0.045 | 3.44 | 3 | <5 | 1.4 | 2022-10-13 | 2022-11-20
2022-11-10 | 0.03 | 0.19 | 0.06 | 4200 | 0.016 | 0.003 | <5 | 0.9 | 256 | 2 | 0.051 | 1.93 | <2 | <5 | 1.61 | 2022-11-17 | 2022-11-22
2022-12-01 | 0.16 | 0.23 | 0.16 | 4240 | 0.009 | 0.014 | <5 | 0.69 | 333 | 4.6 | 0.09 | 8.33 | <2 | 9 | 1.26 | 2022-12-08 | 2022-12-15
2023-01-19 | 0.11 | 0.31 | 0.11 | 3480 | 0.008 | 0.052 | <5 | 0.7 | 279 | 3.8 | 0.069 | 6.12 | 2 | 22 | 1.38 | 2023-01-27 | 2023-01-28
2023-02-02 | 0.1 | 0.32 | 0.17 | 3660 | 0.011 | 0.017 | <5 | 0.69 | 363 | 5.5 | 0.093 | 14 | 2 | <5 | 1.81 | 2023-02-09 | 2023-02-10
2023-03-02 | 0.11 | 1.23 | 0.16 | 3970 | 0.008 | 0.02 | <5 | 0.91 | 303 | 6.5 | 0.086 | 11.3 | <2 | <5 | 2.09 | 2023-03-09 | 2023-03-14
2023-04-06 | 0.04 | 0.24 | 0.17 | 748 | 0.003 | 0.007 | <5 | 0.13 | 55 | 1.8 | 0.044 | 6.02 | <2 | <5 | 0.36 | 2023-04-14 | 2023-04-19
2023-05-04 | 0.03 | 1.55 | 0.13 | 4440 | 0.004 | 0.021 | <5 | 1.63 | 262 | 4.6 | 0.056 | 6.88 | <2 | <5 | 2.26 | 2023-05-10 | 2023-05-17
2023-06-15 | 0.04 | 5.39 | 0.17 | 4290 | 0.006 | 0.156 | <5 | 1.76 | 291 | 9 | 0.051 | 8.72 | <2 | <5 | 1.93 | 2023-06-21 | 2023-06-29
2023-07-06 | 0.12 | 0.69 | 0.19 | 3420 | 0.009 | 0.034 | <5 | 0.66 | 266 | 5.4 | 0.094 | 17.3 | <2 | <5 | 0.78 | 2023-07-12 | 2023-07-14
2023-08-03 | 0.05 | 0.7 | 0.16 | 3920 | 0.008 | 0.006 | <5 | 1.33 | 247 | 4.2 | 0.067 | 9.99 | 2 | <5 | 2.02 | 2023-08-10 | 2023-08-18
2023-09-12 | 0.03 | 0.67 | 0.16 | 3920 | 0.01 | 0.002 | <5 | 1.23 | 238 | 3.7 | 0.058 | 12.2 | <2 | <5 | 1.25 | 2023-09-19 | 2023-09-21
2023-10-03 | 0.22 | 0.28 | 0.19 | 4210 | 0.016 | 0.318 | <5 | 0.91 | 375 | 6 | 0.126 | 32.7 | <2 | 6 | 1.65 | 2023-10-09 | 2023-10-12
2023-11-07 | 0.1 | 0.57 | 0.2 | 4130 | 0.014 | 0.059 | <5 | 2.12 | 325 | 4.6 | 0.069 | 12 | 2 | 8 | 2.24 | 2023-11-14 | 2023-11-16
2023-12-05 | 0.11 | 0.13 | 0.17 | 3980 | 0.013 | 0.005 | <5 | 1.57 | 299 | 3.3 | 0.058 | 10.7 | <2 | 12 | 1.48 | 2023-12-12 | 2023-12-18
2024-01-09 | 0.36 | 0.41 | 0.18 | 3730 | 0.015 | 0.346 | <5 | 0.36 | 321 | 6.4 | 0.098 | 26.9 | 2 | <5 | 0.49 | 2024-01-16 | 2024-01-23
2024-02-06 | 0.2 | 0.23 | 0.21 | 4400 | 0.012 | 0.04 | <5 | 1.34 | 369 | 5.1 | 0.081 | 13.5 | <2 | <5 | 2.08 | 2024-02-14 | 2024-02-21
2024-03-05 | 0.2 | 0.36 | 0.21 | 3800 | 0.016 | 0.071 | <5 | 0.55 | 372 | 8.1 | 0.094 | 25.5 | 5 | <5 | 1.05 | 2024-03-12 | 2024-03-17
2024-04-02 | 0.07 | 0.33 | 0.18 | 5540 | 0.008 | 0.007 | <5 | 2.27 | 349 | 4.6 | 0.042 | 10.8 | 3 | <5 | 2.62 | 2024-04-10 | 2024-04-18
2024-05-07 | 0.29 | 0.21 | 0.22 | 3960 | 0.021 | 0.01 | 5 | 0.84 | 359 | 5 | 0.113 | 27.7 | 4 | 5 | 1.45 | 2024-05-16 | 2024-05-23
2024-06-18 | 0.15 | 0.18 | 0.17 | 3550 | 0.012 | 0.02 | <5 | 0.46 | 296 | 5.5 | 0.075 | 31.8 | 8 | <5 | 0.94 | 2024-06-26 | 2024-07-07
2024-07-02 | 0.13 | 0.16 | 0.15 | 3590 | 0.017 | 0.01 | <5 | 1.16 | 322 | 6.5 | 0.101 | 30.9 | 6 | <5 | 1.65 | 2024-08-05 | 2024-08-29
2024-08-20 | 0.18 | 0.2 | 0.18 | 4320 | 0.015 | 0.01 | <5 | 1.04 | 365 | 6.7 | 0.084 | 36 | <2 | <5 | 1.09 | 2024-08-28 | 2024-08-29
2024-09-03 | 0.17 | 0.25 | 0.16 | 4420 | 0.014 | 0.002 | <5 | 0.85 | 364 | 4.1 | 0.065 | 19.6 | 3 | 8 | 0.92 | 2024-09-10 | 2024-09-17
2024-10-08 | 0.14 | 0.18 | 0.14 | 4400 | 0.018 | 0.006 | <5 | 2.22 | 309 | 4.8 | 0.067 | 20.9 | 5 | <5 | 4.26 | 2024-10-15 | 2024-10-21
2024-11-12 | 0.12 | 0.38 | 0.18 | 4160 | 0.018 | 0.045 | <5 | 1.88 | 372 | 7.2 | 0.106 | 39 | 4 | <5 | 2.41 | 2024-11-20 | 2024-11-30
2024-12-03 | 0.2 | 0.1 | 0.17 | <5 | 0.015 | 0.015 | <5 | 1.41 | 339 | 4 | 0.133 | 17.7 | <2 | <5 | 1.96 | 2024-12-10 | 2024-12-11
2025-01-28 | 0.26 | 0.18 | 0.16 | 4210 | 0.026 | 0.045 | <5 | 1.36 | 359 | 6.6 | 0.111 | 24.9 | <5 | <5 | 3.08 | 2025-02-03
2025-02-18 | 0.16 | 0.16 | 0.22 | 4200 | 0.022 | 0.022 | <5 | 1.12 | 333 | 8.3 | 0.122 | 41.7 | 3 | <5 | 1.78 | 2025-02-25
2025-03-18 | 0.33 | 0.37 | 0.22 | 5220 | 0.019 | 0.015 | <5 | 1.83 | 385 | 3.7 | 0.105 | 42.5 | <2 | <5 | 2.16 | 2025-03-25
2024-04-02 | 0.07 | 0.33 | 0.18 | 5540 | 0.008 | 0.007 | <5 | 2.27 | 349 | 4.6 | 0.042 | 10.8 | 3 | <5 | 2.62 | 2024-04-10
2025-05-06 | 0.21 | 0.12 | 0.17 | 3710 | 0.014 | 0.019 | <5 | 0.55 | 298 | 5.5 | 0.102 | 24.3 | 2 | <5 | 1.12 | 2025-05-13 | 2025-05-22
2025-06-06 | 0.17 | 0.32 | 0.16 | 4120 | 0.016 | 0.049 | <5 | 1.17 | 300 | 5.5 | 0.081 | 27.1 | 5 | 8 | 2.02 | 11&13/06/2025
2025-07-08 | 0.14 | 0.56 | 0.17 | 3770 | 0.021 | 0.044 | <5 | 1.28 | 315 | 6.4 | 0.113 | 28 | 4 | <5 | 3 | 2025-07-15
2025-08-05 | 0.08 | 0.21 | 0.13 | 3750 | 0.014 | 0.002 | <5 | <0.01 | 227 | 3.6 | 0.066 | 10.8 | 4 | <5 | 3.68 | 2025-08-12
2025-09-02 | 0.08 | 0.16 | 0.18 | 3440 | 0.012 | 0.001 | <5 | 0.85 | 225 | 2.2 | 0.039 | 5.31 | 2 | 5 | 1.3 | 2025-09-08
2025-10-07 | 0.18 | 0.17 | 0.14 | 3150 | 0.016 | 0.061 | <5 | 1.3 | 286 | 8 | 0.134 | 59.2 | 4 | <5 | 2.07 | 2025-10-13
Units | Description | [7 empty] | Licensee Name | Sydney Olympic Park Authority.
mg per L | Milligrams per Litre - the amount, in milligrams, of a pollutant per litre of substrate measured. | [7 empty] | Licensee Address | Locked Bag 3, SYDNEY OLYMPIC PARK, NSW 2127
[9 empty] | Location of Monitoring Point 3 | Submerged approxmately 3m from the edge of embankment as described by map titled "Sydney Olympic Park RO Discharge Plan Drawing No. 001-P-P-0687 Rev.B" dated 28/8/06.
The WRAMS Licence can be viewed in full on the NSW EPA website:
http://www.epa.nsw.gov.au/prpoeoapp/ViewPOEOLicence.aspx?DOCID=29838&SYSUID=1&LICID=10020
NOTE: This document is available at www.sopa.nsw.gov.au and is uncontrolled once downloaded and/or printed.

## WRAMS 10020 Discharge Point 4
WRAMS DISCHARGE DATA
ENVIRONMENTAL PROTECTION LICENCE 10020.
WRAMS DISCHARGE POINT 4
Monitoring Frequency | Daily during any discharge.
Method | Grab sample, and, method approved in writing by the Authority.
Volume Limit | 7000 (kL per day).
Parameter / Pollutant | Daily Volume | TSS | BOD | Faecal Coliforms | Total Phosphorus | Total Nitrogen | pH | Oil and Grease | Chlorine
Unit of measurement | (kL per Day) | (mg per L) | (mg per L) | (CFU per 0.1L) | (mg per L) | (mg per L) | (pH units) | (mg per L) | (mg per L)
80 percentile concentration limit | N/A | Nil | Nil | 1000 | Nil | Nil | Nil | Nil | Nil
90 percentile concentration limit | N/A | Nil | 40 | Nil | Nil | 10 | Nil | Nil | Nil
100 percentile concentration limit | N/A | 50 | 20 | 4000 | 1 | 12 | 6.5 - 8 | 10 | 0.5
Date Sampled | [9 empty] | Date Received | Date Published
2015-04-22 | 6000 | 20 | 3 | 200 | 0.8 | 3.7 | 8.13 | 5 | <0.2 | 2015-04-30 | 2015-06-16
2015-04-23 | 6000 | 12 | <2 | 130 | 0.94 | 3.2 | 8.19 | <5 | <0.2 | 2015-05-01 | 2015-06-16
2015-04-24 | 6000 | 8 | <2 | 64 | 0.94 | 3.2 | 8.05 | <5 | <0.2 | 2015-05-01 | 2015-06-16
2015-04-25 | 6000 | 12 | 3 | 11 | 1 | 1.4 | 8.04 | <5 | <0.2 | 2015-05-05 | 2015-06-16
2015-04-27 | 6000 | 12 | 3 | 11 | 1 | 1.4 | 8.04 | <5 | <0.2 | 2015-05-05 | 2015-06-16
2015-04-30 | 6000 | 8 | <2 | 100 | 0.9 | 3 | 8.21 | <5 | <0.2 | 2015-05-07 | 2015-06-16
2020-02-09 | 4833 | 13 | 5 | 140 | 0.33 | 1.5 | 7.95 | <5 | <0.2 | 2020-05-21
2020-02-10 | 4833 | 24 | 6 | 70 | 0.3 | 1.4 | 7.97 | 5 | <1 | 2020-05-21
2020-02-11 | 4833 | 13 | 3 | 160 | 0.8 | 1.2 | 8.01 | <5 | <0.2 | 2020-05-24
2020-02-12 | 4833 | 12 | 6 | 66 | 0.26 | 1.2 | 7.99 | <5 | <0.2 | 2020-05-24
2020-02-13 | 4833 | 11 | 8 | 52 | 0.27 | 1.2 | 7.51 | <5 | 0.08 | 2020-05-24
2020-07-27 | 4185 | <5 | 2 | 51 | 0.32 | 1.9 | 7.55 | <5 | <0.2 | 2020-08-03
2020-07-28 | 6480 | <5 | <2 | 30 | 0.35 | 1.8 | 7.62 | 5 | 0.03 | 2020-08-04
2020-07-29 | 2160 | <5 | 3 | 30 | 0.36 | 1.8 | 6.9 | <5 | 0.05 | 2020-08-05
2020-08-10 | 4050 | <5 | 2 | 26 | 0.34 | 1.6 | 7.93 | <5 | 0.08 | 2020-08-17
2020-08-11 | 6480 | <5 | 2 | 8 | 0.36 | 1.5 | 7.76 | <5 | 0.02 | 2020-08-19
2020-08-12 | 6480 | <5 | 3 | 16 | 0.4 | 1.8 | 7.14 | 5 | <0.2 | 2020-08-19
2020-08-13 | 6480 | <5 | 2 | 11 | 0.32 | 2 | 7.22 | <5 | <0.2 | 2020-08-20
2021-03-20 | 2295 | 7 | <2 | 160 | 0.5 | 1.5 | 7.66 | <5 | 0.21 | 2021-03-29
2021-03-21 | 6480 | 11 | 2 | 160 | 0.43 | 1.4 | 7.77 | <5 | 0.24 | 2021-03-29
2021-03-22 | 6480 | 11 | <2 | 110 | 0.44 | 1.5 | 7.8 | <5 | 0.2 | 2021-03-29
2021-03-23 | 6480 | 10 | 29 | 40 | 0.41 | 1.5 | 7.89 | <5 | 0.13 | 2021-03-30
2021-03-24 | 6480 | 10 | 7 | 58 | 0.45 | 1.5 | 7.87 | <5 | 0.13 | 2021-03-30
2022-02-24 | 4050 | 11 | 5 | 520 | 0.35 | 1 | 7.34 | <5 | 0.41 | 2022-03-02
2022-02-26 | 2160 | 8 | 2 | 290 | 0.32 | 0.9 | 7.68 | <5 | 0.42 | 2022-03-07
2022-02-27 | 3645 | 10 | <2 | 88 | 0.29 | 0.8 | 7.82 | <5 | 0,4 | 2022-03-07
2022-02-28 | 6480 | 11 | <2 | 170 | 0.3 | 0.8 | 7.78 | <5 | 0.39 | 2022-03-07
2022-03-01 | 6480 | 9 | <2 | 70 | 0.35 | 1 | 7.6 | <5 | 0.37 | 2022-03-08
2022-03-03 | 6480 | 10 | 2 | 110 | 0.31 | 0.9 | 7.55 | <5 | 0.3 | 2022-03-10
2022-03-04 | 6480 | 10 | 2 | 74 | 0.24 | 0.7 | 7.81 | <5 | 0.3 | 2022-03-11
2022-03-05 | 6480 | 8 | <2 | 18 | 0.4 | 0.8 | 7.69 | <5 | 0.28 | 2022-03-14
2022-03-07 | 4590 | <5 | <2 | 44 | 0.31 | 0.8 | 7.63 | <5 | 0.26 | 2022-03-14
2022-03-08 | 6480 | 6 | 4 | 34 | 0.23 | 0.9 | 7.95 | <5 | 0.22 | 2022-03-16
2022-03-09 | 6480 | 11 | 3 | 39 | 0.17 | 0.7 | 8.02 | 5 | 0.17 | 2022-03-16
2022-03-10 | 6480 | 8 | <2 | 40 | 0.18 | 0.5 | 7.51 | <5 | <0.2 | 2022-03-17
2022-04-07 | 3105 | 7 | 3 | 45 | 0.22 | 0.5 | 7.95 | <5 | 0.09 | 2022-04-19
2022-04-08 | 6480 | 8 | 3 | 48 | 0.21 | 0.5 | 7.65 | <5 | 0.18 | 2022-04-19
2022-07-03 | 5762 | 6 | 3 | 68 | 0.21 | 1 | 7.6 | <5 | <0.2 | 2022-07-11
2022-07-04 | 6931 | 7 | 2 | 52 | 0.2 | 1 | 7.85 | <5 | <0.2 | 2022-07-11
2022-07-05 | 6931 | 5 | 2 | 63 | 0.18 | 1 | 7.99 | <5 | <0.2 | 2022-07-13
2022-07-06 | 6931 | 6 | 2 | 64 | 0.18 | 1 | 7.99 | <5 | <0.2 | 2022-07-13
2022-07-07 | 6931 | <5 | <2 | 46 | 0.2 | 1.1 | 7.97 | <5 | <0.2 | 2022-07-14
Units | Description | [6 empty] | Licensee Name | Sydney Olympic Park Authority.
mg per L | Milligrams per Litre - the amount, in milligrams, of a pollutant per litre of substrate measured. | [6 empty] | Licensee Address | Locked Bag 3, SYDNEY OLYMPIC PARK, NSW 2127
CFU per 0.1L | Colony Forming Units per one hundred millilitres of substrate. | [6 empty] | Location of Monitoring Point 4 | Brickpit Reservoir, at the end of the discharge pipe into culvert as shown in drawing 001-P-P-3358 REV D dated 25 January 2015
kL per day | Kilolitres discharge daily for every discharge.
The WRAMS Licence can be viewed in full on the NSW EPA website:
http://www.epa.nsw.gov.au/prpoeoapp/ViewPOEOLicence.aspx?DOCID=29838&SYSUID=1&LICID=10020
NOTE: This document is available at www.sopa.nsw.gov.au and is uncontrolled once downloaded and/or printed.
<5